## Commercial shell and core
MEP take-offs spreadsheet
Section F2.1 At the early design phase
This tab is to be read in parallel with RICS PS Appendix F
If no information regarding MEP quantities is available from the QS or the MEP engineers at the concept design phase, the following table can be used for embodied carbon assessments for commercial shell and core buildings. The table lists average MEP take-off assumptions according to the information that should be availible from an MEP engineer at the early design phase. It is based on a medium-sized commercial building in the UK.
Commercial shell and core
MEP categories | Information to be provided by MEP engineer at concept stage | What take-offs assumptions you can make if no QS information is available
|  | Based on mid sized commercial office with centralised plant systems | If the plant systems are not centralised the following assumptions should be used
5.1.2.1 Cold water systems | - system type of storage and size (at least for storage tank and calorifiers) - type of cold water distribution (copper or pex or plastic) - if there is a boosterpump or not? - rainwater harvesting or not? system strategy and space provision - greywater harvesting or not? system strategy and space provision (including fixture points) - foul drainage piping preference: cast iron, HDPE, PVC - rainwater drainage piping preference: cast iron or PVC - water treatment strategy? | Cold water distribution For BCWS riser and mains distribution assume 50m per level, average size 35mm diameter For secondary BCWS distribution to fixtures assume 6m per fixture point, average size 15mm, plus 1No. ball valve and 1No. flex connection per fixture Cold water control and ancillaries Allow 1No. water meter per office or retail tenant, and 5No. additional landlord water meters Allow 1No. booster pumpset for BCWS if required by engineers Allow 1No. water shut off valve per toilet block | Cold water distribution For BCWS riser and mains distribution assume 50m per level, average size 35mm diameter For secondary BCWS distribution to fixtures assume 6m per fixture point, average size 15mm, plus 1No. ball valve and 1No. flex connection per fixture For secondary BCWS distribution to local elec. water heaters assume 6m per equipment, average size 20mm, plus 1No. ball valve and 1No. flex connection per fixture
5.1.2.2 Cold water storage |  | Allow for 1No. tank, water conditioner, UV filtration Allow 2No. packaged Cat 5 break tank and pump sets
5.1.3.1 Surface water/rainwater/foul water drainage |  | Surface water/rainwater drainage Assume 90m per level for rainwater system, average size 110mm diameter (if no information by engineer) Foul water drainage Assume 115m per level for soil, waste and vent stacks and main distribution, average size 110mm diameter (if no information by engineer) For secondary distribution to fixtures assume 4m per fixture point, average size 75mm, for miscellaneous systems, such as condensate, drains, etc. allow 0.03m of 100mm pipework per m2
5.1.3.2 Water reuse systems |  | If you have grey water management Assume 80m per level for grey water collection stacks and main distribution, average size 110mm diameter (if no information by engineer) For grey water riser and mains distribution assume 50m per level, average size 35mm diameter For secondary grey water collection distribution to fixtures assume 4m per fixture point, average size 75mm For secondary grey water distribution to fixtures assume 6m per fixture point, average size 15mm, plus 1No. ball valve and 1No. flex connection per fixture If you have rainwater harvesting Assume 100m per level for rainwater system, average size 110mm diameter For rainwater riser and mains distribution assume 50m per level, average size 35mm diameter For secondary rainwater distribution to fixtures assume 6m per fixture point, average size 15mm, plus 1No. ball valve and 1No. flex connection per fixture
5.2.1.1 Heat and hot water generation equipment | - total building load in kW - type of heating system and capacity - centralised or individual/decentralised - type of storage (but no size) - heat emitter options (but no size) | Heat generation If no load information provided by the engineers assume 60-80w per m2 for primary heat pump plant Hot water plant Assume 2No. storage calorifiers and 1No. pump | Hot water plant Allow 1No. local elec. water heater per toilet block
5.2.1.2 Heat and hot water distribution, control, ancillaries, emitters, exchangers/terminal units |  | Hot water distribution For centralised system: HWS riser and mains distribution assume 60m per level, average size 28mm diameter For secondary HWS distribution to fixtures assume 10m per fixture point, average size 15mm, plus 1No. ball valve, 1No. thermostatic mixing valve and 1No. flex connection per fixture point Heat distribution Allow 1m of LTHW 100mm diameter pipework per 29 GIA m2 for primary and secondary LTHW pipework Allow valve sets per each main piece of plant/terminal device Heat emitter In landlord area: allow for underfloor heating to main reception, air curtains to main entrances, trench heating to any double height spaces, and allow 1No. radiator per 100m2 Heat exchanger In landlord area: Allow 1No. per office tenancy if required Allow 1No. per retail unit for high rise buildings consider allowing PHXs on main branch Heat and hot water ancillaries and control Allow for 1No. primary set of pumps Allow for secondary pump set (2 to 3Nos.) 1No. pressurisation unit, dosing pot, deaearator unit, dirt separator Allow 10No. primary heat meters and 1no. per office/retail tenancy | Hot water distribution For secondary HWS distribution to fixtures assume 10m per fixture point, average size 15mm, plus 1No. ball valve, 1No. thermostatic mixing valve and 1No. flex connection per fixture point
5.2.1.3 Heat storage equipment |  | Allow 2No. LTHW buffer vessels with the size given by the engineers
5.2.2.1 Cooling generation equipment | - active cooling or not? - type of systems | Reversible heat pump generates cooling, so no additional plant needed
5.2.2.2 Cooling emitter, exchangers/ terminal units, ancillaries and control, distribution, storage |  | Cooling exchangers Allow 1No. per office tenancy if required, Allow 1No. per retail unit, For high rise buildings consider allowing PHXs on main branch Cooling ancillaries and control Allow for 1No. primary set of pumps Allow for secondary pump set (2 to 3Nos.) 1No. pressurisation unit, dosing pot, deaearator unit, dirt separator Allow 10No. primary heat meters and 1no. per office/retail tenancy Cooling distribution Allow 1m of CHW 125mm diameter pipework per 29 GIA m2 for primary and secondary CHW pipework Allow valve sets per each main piece of plant/terminal device Cooling storage Allow 2No. CHW buffer vessels If fan coils Allow for 1No. fan coil units per lift lobby Allow 1No. fan coil unit per 25m2 for reception area, trench cooling to double height glazed facades Allow 10No. dedicated cooling units like FCU or DX split unit (for miscellaneous landlord FM rooms, MERs, plant rooms, etc.)
5.2.3 Air movement | - what air movement systems in the building and approximate size and number of units - kitchen extract – yes or no? indicative size and number of units - number and size of external louvres - fire safety requirements | Allow air handling units total load at 2.0/l/s/NIA m² for Cat A office areas (if no design data) Allow 1.5/l/s/ms (basement) for basement air handling unit Allow for 5No. MVHR units for miscellaneous areas Allow 1 twin toilet extract fans per toilet riser Allow for 5No. small fans for miscellaneous areas | Allow local/on floor air handling units per office tenant (if no design data) Allow 1.5/l/s/ms (basement) for basement air handling unit Allow for 5No. MVHR units for miscellaneous areas Allow 1 twin toilet extract fans per toilet riser Allow for 5No. small fans for miscellaneous areas
5.2.4.1 Air terminals |  | Allow 1No. grille per 350/GIA m2 Allow 1No. CAV/VAV per office tenancy | Allow 1No. grille per 350/GIA m2 Allow 1No. CAV/VAV per office tenancy
5.2.4.2 Ductwork and ancilleries |  | Allow for 1m2 surface area of plain ductwork including insulation per 5/GIA m2 for whole office fresh air ventilation, assume 1mm thickness Allow aliclad to 15% of ductwork area with 0.5mm thickness Allow for 1m2 surface area of plain ductwork per 60/GIA m2 for miscellaneous ventilation ductwork, assume 1mm thickness | Allow for 80m2 surface area of plain ductwork including insulation per on floor office AHU, assume 1mm thickness Allow aliclad to 15% of ductwork area with 0.5mm thickness Allow for 1m2 surface area of plain ductwork per 60/GIA m2 for miscellaneous ventilation ductwork, assume 1mm thickness
5.2.4.3 Control dampers, attenuation and fIre safety related to ventilation equipment |  | Control damper Allow 1No. motorised damper per office tenancy Allow for 1No. damper per 300/GIA m2 for miscellaneous dampers Attenuation Allow for 4No. attenautors per office ventilation system Allow 1No. per tenancy duct branch off, and an additional 20No. for miscellaneous systems Fire safety Allow for mechanical smoke extract system per level per fire fighting stair Allow for a roof mounted smoke extract fan set per fire fighting stair Allow 25m2 per level of fire rated ductwork for Smoke lift lobby system Allow 1m2 of fire rated ductwork per 1.9m2 of basement, assume 1mm thickness Allow 1No. motorised damper per 15m2 of basement Allow 2No. basement smoke extract fans | Control damper Allow 1No. motorised damper per office tenancy Allow for 1No. damper per 300/GIA m2 for miscellaneous dampers Attenuation Allow for 4No. attenautors per on floor office AHU Allow 1No. per tenancy duct branch off, and an additional 20No. for micellaneous systems
5.3.1.1 Internal lighting | - LED or not? - options of fittings but nothing decided - lighting control strategy: daylight dimming? etc. (unspecified quantities) | Allow for 1No. lighting fixture per 4m2 of landlord area (GIA-NIA) Allow 1m of linear lighting per 5m2 of landlord area Allow 25m lighting cabling per fixture Allow, for lighting control: 1No. LCM per 30m2, 1No. PIR sensor per 30m2 NIAm2 (landlord spaces, i.e. GIA less NIA m2)
5.3.1.2 External lighting (building mounted) |  | Allow 1No. external light per 80/GIA m2 Allow 40m of lighting cabling per fixture
5.3.1.3 Emergency lighting |  | Allow additional 25% of total lights to be emergency lights
5.3.1.4 Other lighting |  | N/A
5.3.2.1 Electrical power | - max total building demand in kVA - type of cabling (unspesified quantity) | Small power Allow for 1No. small power points per 22m2 GIA allow 10m of cable per power point Power low voltage life safety Allow 27VA per GIA m2 for life safety generator Allow 1000A main life safety switchpanel with 15No. ways; submains Allow for 15No. automatic transfer switches Power low voltage Allow 0.135A per GIA m2 for main switchpanel Allow 1No. split distribution board and 1No. mechanical distribution board per office tenancy Allow 1No. landlords distribution board per 3No. levels Allow 1No. miscellaneous distribution board per 2,300/GIA m2 Allow for tenant rising busbar per tenancy split Allow for tap offs aligned with distribution boards; submains Power containment Allow for 1m of 200mm cable tray including fittings per 9/GIA m2 for shell and core containments and risers If high voltage required For every 750 kVa allow: 1No. transformer plus ring main unit plus high voltage switch gear plus high voltage distribution
5.3.2.2 ELV/communications/security |  | Security Allow for security head end (rack, server) Allow 1No. CCTV camera per 450/GIA m2 Allow 1No. access control door per 500/GIA m2 Allow for intruder alarm device per 950/GIA m2 Allow for 10No. intercom points COMMUNICATION AV equipment - N/A (usually not provided for Landlord use). By future tenant Cat B works. Allow for 1no. Induction loop per reception area
5.3.2.3 IT and data | - what areas require data | Landlord Wifi/WAP: allow for 1Nos. per m2 of landlord area (GIAm2 – less Cat A/retail NIA m2) Allow 1No. data points per 40 to 50/m2 GIA for landlord IT cabling Allow for 2No. data cabinet per every 3No. floor for landlord IT equipments
5.3.2.4 BMS | - BMS control or not? | Allow 5No. main control panels for main plant, and 1No. small panel per floor. Assume 1 point per 15/GIA m2 Allow 25m of control cabling per point
5.3.2.5 Electricity back up generation | - UPS or not? but no more info - battery or not? but no more info - generator or not? rough size and number of units | Allow for 10-20KVA, 10min. static local UPS for landlord comms
5.3.2.6 Fire detection and alarm | - level of coverage (L1/ L2/.../M) - if PAVA required or not | Allow 1No. main fire alarm panel, fire indicator panel Allow 1No. field device per 28/GIA m2 Allow 30m of fire alarm cable per device If PAVA required, allow for PAVA panel, 1No. speaker per 130/GIA m2 Allow 1No. emergency voice communication outstation per 700m2 Allow 1No. disabled refuge system per fire escape stair and 1no. main panel Allow 1No. disabled alarm per Doc M WC/shower
5.4.1.1 Renewable energy – electrical generation onsite and building mounted | - PV: total M2 of panels, type, optimiser or not? type of battery and approximate size - wind turbine: yes or no? quantity - water turbine: yes or no? quantity | Where information is not available: allow for 1m2 of photovoltaics panel per 2 m2 of building footprint
5.4.1.2 Renewable energy – Storage onsite |  | Not applicable
5.5.1.1 Sprinkler system | - Fire strategy to know what system is included but no sizes | Allow 180m3 of sprinkler tanks and 3Nos. sprinkler pumps Allow 150m main distribution pipeworks plus 4m of pipeworks riser per floor at average size 100mm diam Allow zone valves, 1No. per office and retail tenants, 1No. per floor for landlord zone valves, add extra 3No. miscellaneous zone valves Allow 1No. sprinkler heads per 12m2 of landlord spaces (GIA less NIA m2) Allow 3m of 20mm diam. pipeworks average per sprinkler heads
5.5.1.2 Fire fighting systems |  | Dry riser Allow 2No. dry riser inlets Allow 1No. dry riser outlet per floor per fire fighting stair Allow 10m of 100mm pipework including fittings per dry riser outlet AOV Allow 1No. per fire fighting stair Fire suppression Allow for gaseous fire suppression to MER room: copper piping, gas balls, valves and nozzles
5.5.1.3 Lightning protection/earth bonding | - lightning protection or not? | Allow for 1m of Cu/Al tape per 16m2 GIA
5.5.2.1 Fuel installations |  | Assume no gas works Allow 100m of 40mm diameter fuel pipe, fuel tank and pumpset
5.5.2.2 Lift, stair lift, lifting platform | - number of lifts plus size (nb people/lift) - number of escalators plus size (floor to ceiling height) - number of moving walks plus size (floor to ceiling height) - number of stairlifts | No additional information required
5.5.2.3 Escalators and moving walkways
Note: This table does not include sanitaryware – this may be updated in the future

## Commercial Cat A
This tab is to be read in parallel with RICS PS Appendix F
If no information regarding MEP quantities is available from the QS or the MEP engineers at the concept design phase, the following table can be used for embodied carbon assessments for commercial buildings in their Cat A phase. The table lists average take-off assumptions according to the information that should be availible from an MEP engineer at the early design phase. It is based on a medium-sized commercial building in the UK.
Commercial Cat A
MEP categories | Information to be provided by MEP engineer at Concept Stage | What take-offs assumptions you can make if no QS information is available. This is an example based on mid-sized commercial office with 4 pipe fan coil units and centralised ductwork distributed at high level
5.1.3.1 Surface water/rainwater/foul water drainage |  | Foul water drainage Allow for 7m of condensate drain per 32m2 NIA, average 20mm diam
5.2.1.1 Heat and hot water distribution, control, ancillaries, emitters, exchangers/terminal units | - system type and zoning | Allow for 15m of 20mm diameter LTHW pipework including insulation per 32m2 NIA of tenant area Allow for 1No. FCU per 32m2 NIA
5.2.2.2 Cooling emitter, exchangers/terminal units, ancillaries and control, distribution, storage | - system type and zoning | Allow for 15m of 25mm diameter CHW pipework per 32m2 NIA
5.2.3 Air movement | - system type and approximate size
5.2.4.1 Air terminals |  | Allow for 4No. supply grilles per 32m2 NIA
5.2.4.2 Ductwork and ancilleries |  | Allow for 1m2 surface area of plain ductwork including insulation per 4.5m2 NIA for office fresh air ventilation, assume 1mm thickness (primary ductwork) Allow for 10m of 200mm diameter circular ductwork per 32m2 NIA, assume 1mm thickness (secondary ductworks)
5.2.4.3 Control dampers, attenuation and fIre safety related to ventilation equipment |  | Allow 5No. VCD per 32m2 NIA
5.3.1.1 Internal lighting | - lux levels - lighting control strategy - areas requiring emergency lighting | Allow for 1No. lighting fixture per 3m2 of NIA Allow 1No. exit light per office tenant main door Allow 25m lighting cabling per fixture Lighting control Allow 1No. LCM per 30m2 NIA, 1no. PIR sensor per 30m2 NIAm2 (Cat A fitout)
5.3.1.3 Emergency lighting |  | Allow additional 25% of total lights to be emergency lights
5.3.2.1 Electrical power | - maximum demand (kVA) - primary distribution routes - BMS: yes/no | Small power Allow for 1No. small power points per 10m2 NIA allow 6m of cable per power points Allow for 1No. Power supply to FCU per 32m2 Allow 1No. Cleaners socket per 50m2 NIA Power containment Allow for 1m of 200mm cable tray including fittings per 20/NIA m2 (lighting and power) Allow for 1m of 200mm cable tray including fittings per 20/NIA m2 (comms like FA, BMS)
5.3.2.4 BMS |  | Allow for 1No. FCU unitary controller per 32m2 NIA of tenant area Allow 35m of cabling to the outstation per controller
5.3.2.6 Fire detection and alarm | - level of coverage - PAVA required: yes/no | Allow 1No. smoke detector with sounder per 25/m2 NIAm2 Allow No. breakglass unit per office tenant doors if PAVA required, allow 1No. PAVA speaker per 130/GIA m2
5.5.1.1 Sprinkler system | - yes/no | Allow 1No. sprinkler heads per 9m2 of NIA Allow 3m of 20mm diam. pipeworks average per sprinkler heads
Note: IT and data cabling and security to be included in Cat B
Note: This table does not include sanitaryware – this may be updated in the future

## Residential
This tab is to be read in parallel to RICS PS Appendix F
If no information regarding MEP quantities is available from the QS or the MEP engineers at the concept design phase, the following table can be used for embodied carbon assessments for residential buildings. Assumptions according to the information that should be availible from an MEP engineer at the early design phase.
Residential
MEP categories | Information to be provided by MEP engineer at concept stage | What take-offs assumptions you can make if no QS information is available. (This example is based on 7 floor residential block with centralised heating and hot water provided by heat pumps with underfloor heating.)
|  | Landlord areas | Tenant areas
5.1.2.1 Cold water systems | - system type of storage plus size (at least for storage tank and calorifiers) - type of cold water distribution (copper or pex or plastic) - if there is a boosterpump or not? - rainwater harvesting or not? system strategy plus space provision - greywater harvesting or not? system strategy plus space provision (including fixture points) - foul drainage piping preference: cast iron, HDPE, PVC - rainwater drainage piping preference: cast iron or PVC - water treatment strategy? | For BCWS riser and mains distribution assume 40m per level, average size 35mm diameter | Assume 5m per connection to kitchen sanitaryware and bathroom pods
|  | For secondary BCWS distribution to landlord fixtures assume 6m per fixture point, average size 15mm, plus 1No. ball valve and 1No. flex connection per fixture | Count number of bathrooms and kitchens.
5.1.2.2 Cold water storage |  | Allow for 1no. tank, water conditioner, UV filtration, Allow 1No. packaged Cat 5 break tank and pump sets | N/A
|  | Allow 1No. Incoming water meter and 2No. additional landlord water meters Allow 1No. booster pumpset for BCWS if required by engineers | Allow for 1No. water meter to each appartment
5.1.3.1 Surface water/rainwater/foul water drainage |  | Count number of risers, assume 4m length of pipe average size 110mm diameter (if no information by engineer) | Allowance of 3m average size 75mm for rainwater per residential balcony
|  | Assume 80m per level for soil, waste and vent stacks and main distribution, average size 110mm diameter (if no information by engineer) | For secondary distribution to fixtures assume 4m per fixture point, average size 75mm, for miscellaneous systems, such as condensate, drains etc. allow 0.03m of 100mm pipework per m2
5.1.3.2 Water reuse systems
5.2.1.1 Heat and hot water generation equipment | - total building load in kW - type of heating system plus capacity - centralised or individual/decentralised - type of storage (but no size) - heat emitter options (but no size) | If no load information provided by the engineers: Assume 60-80w per m2 for primary heat pump plant
|  | Allow for 1No. primary set of pumps Allow for secondary pump set (2 to 3nos.) 1No. pressurisation unit, dosing pot, deaearator unit, dirt separator | n/a Circulation included in HIU
5.2.1.2 Heat and hot water distribution, control, ancillaries, emitters, exchangers/terminal units |  |  | For secondary HWS distribution to fixtures assume 10m per fixture point, average size 15mm, plus 1No. ball valve, 1No. thermostatic mixing valve and 1No. flex connection per fixture point
|  | In landlord area: Allow for underfloor heating to main reception, Air curtains to main entrances | Allow UFH to 90% of appartment NSA.
Allow 1No. HIU per appartment
|  | Allow 1m of LTHW 100mm diameter pipework per 35 GIA m2 for primary distribution Secondary LTHW pipework allow 80m average size 32mm per floor Allow valve sets per each main piece of plant/terminal device | Allow 1No. heat meter to each appartment, allow valve sets to each apartment Allow 1No. UFH manifold to each apartment
5.2.1.3 Heat storage equipment |  | Allow 2No. LTHW buffer vessels with the size given by the engineers | No storage as water direct from HIU
5.2.2.1 Cooling generation equipment | - do you have active cooling or not? - type of systems | N/A | N/A
5.2.2.2 Cooling emitter, exchangers/ terminal units, ancillaries and control, distribution, storage
5.2.3 Air movement | - what air movement systems in the building plus approximate size plus number of units - kitchen extract – yes or no? indicative size plus number of units - number and size of external louvres - fire safety requirements | Allow air handling unit to residential lobby (if no design data) Allow 1.5/l/s/ms (basement) for basement air handling unit Allow for 3No. small fans for miscellaneous areas (bin stores etc.) | Assume 1nr MVHR unit per apartment (up to 3bed)
5.2.4.1 Air terminals |  | Allow 1No. grille per 500/GIA m2 | Allow 1No. grille per 10/ m2 NSA
5.2.4.2 Ductwork and ancilleries |  | Assume 1 m2 (surface area) of ductwork per 90 m2 of GIA, assume 1mm thickness | Assume 1 m2 (surface area) of ductwork per m2 of apartment NSA
5.2.4.3 Control dampers, attenuation and fIre safety related to ventilation equipment |  | Allow 1No. VCD per grille Allow for 1No. damper per 300/GIA m2 for miscellaneous dampers | N/A
|  | Allow for 4No. Attenautors per ventilation system. Allow 2No. When supply or extract only. Allow 1No. per tenancy duct branch off and an additional 20No. for micellaneous systems | Allow for 4No. attenautors per MVHR unit
5.3.1.1 Internal lighting | - LED or not? - type of fitting - lighting control strategy: daylight dimming? etc. but no quantities | Allow for 1No. lighting fixture per 8m2 of landlord area (GIA-NIA) Allow 25m lighting cabling per fixture | Allow for 1No. lighting fixture per 5m2 of NSA Allow 25m lighting cabling per fixture
5.3.1.2 External lighting (building mounted) |  | Allow 1No. external light per 80/GIA m2; Allow 40m of lighting cabling per fixture
5.3.1.3 Emergency lighting |  | Allow additional 25% of total lights to be emergency lights | N/A
5.3.1.4 Other lighting |  | Allow 1No. external light per 80/GIA m2 Allow 40m of lighting cabling per fixture
5.3.2.1 Electrical power | - max total building demand in - type of cabling (unspecified quantity) | Allow 0.423A per GIA m2 for main switchpanel Allow 1No. landlord's distribution board per 3No. levels Allow 1No. miscellaneous DB per 2,300/GIA m2 Allow for rising busbar 4m per floor Allow for tap offs aligned with distribution boards Submains: allow for 15m submains cabling to each apartment | Allow 1No. consumer unit per apartment
|  | Allow for 1No. small power points per 60m2 GIA include 20m of cabling per power point | Allow for 1No. small power points per 2m2 NSA include 3m of cabling per power point
|  | Allow for 4m of 200mm cable tray including fittings per GIA m2 for shell and core containment and risers | N/A
5.3.2.2 ELV/communications/security |  | Allow 1No. data points per 40 to 50/m2 GIA for landlord IT cabling | Allow 2No. data points per apartment, assumes tenant provided WiFi
|  | Allow for security head end (rack, server) Allow 1No. CCTV camera per 250/GIA m2; Allow 1No. access control door to main entrance and 1No. per level per core Allow for 1No. intercom point to main door | Allow 1No. intercom unit per aparment. Allow 1No. telephone outlet per aparment Allow 1No. media plate per apartmet/living room
|  | AV equipment – N/A (usually not provided for landlord use) | N/A
5.3.2.3 IT and data | - what areas require data
5.3.2.4 BMS | - BMS control or not?
5.3.2.5 Electricity back up generation | - UPS or not? but no more info - Battery or not? but no more info - Generator or not? rough size and number of units | Allow 20VA per GIA m2 for life safety generator Allow 1000A main life safety switchpanel with 15No. ways Submains: allow for 5No. automatic transfer switches | N/A
|  | UPS allowance per kVA | Not applicable
5.3.2.6 Fire detection and alarm | - level of coverage (L1/ L2/.../M) - if PAVA required or not | Allow 1No. main fire alarm panel, fire indicator panel Allow 1No. field device per 50/GIA m2 Allow 30m of fire alarm cable per device If PAVA required, allow for PAVA panel, 1No. speaker per 130/GIA m2 Allow 1No. emergency voice communication outstation per 700m2 Allow 1No. disabled refuge system per fire escape stair and 1No. main panel | Allow 1No. field device per 10/GIA m2 Allow 30m of fire alarm cable per device
5.4.1.1 Renewable energy – Electrical generation onsite and building mounted | - PV: total M2 of panels, type, optimiser or not? type of battery plus approximate size - wind turbine: yes or no? quantity - water turbine: yes or no? quantity | Where information is not availible – allow for 1m2 of photovoltaics panel per 2 m2 of building footprint | Not applicable
5.4.1.2 Renewable energy – Storage onsite |  | N/A | N/A
5.5.1.1 Sprinkler system | - fire strategy to know what systems are included (unspecified size) | Sprinkler tank by volume m3 Allow 150m main distribution pipework plus 4m of pipework riser per floor at average size 100mm diam Allow zone valves, 1No. per 1No. per floor for landlord zone valves, add extra 2Nos. miscellaneous zone valves Allow 1No. sprinkler head per 12m2 of landlord spaces (GIA less NIA m2) | Allow 1No. sprinkler head per 12m2 of NSA Allow 3m of 20mm diam. pipework per sprinkler head
Allow 3m of 20mm diam. pipework per sprinkler head
5.5.1.2 Fire fighting systems |  | For dry riser allow 2No. dry riser inlets | Not applicable
Allow 1No. dry riser outlet per floor per fire fighting stair
Allow 10m of 100mm pipework including fittings per dry riser outlet
|  | Allow for mechanical smoke extract system per level per fire fighting stair Allow for a roof mounted smoke extract fan set per fire fighting stair Allow 25m2 per level of fire rated ductwork for smoke lift lobby system Allow 1m2 of fire rated ductwork per 1.9m2 of basement, assume 1mm thickness Allow 1No. motorised damper per 15m2 of basement Allow 2No. basement smoke extract fans | N/A
5.5.1.3 Lightning protection/earth bonding | - lightning protection or not? | Allow for 1m of Cu/Al tape per 16m2 GIA | Allow for 1m of Cu/Al tape per 16m2 NSA
5.5.2.1 Fuel installations |  | Assume no gas works | Assume no gas works
5.5.2.2 Lift, stair lift, lifting platform | - number of lifts plus size (nb people/lift) - number of escalators plus size (floor to ceiling height) - number of moving walks plus size (floor to ceiling height) - number of stairlifts | No additional information than the one given by the engineers Approx size by floor area/type and number of floors to estimate lift capacity and speed. | Not applicable
5.5.2.3 Escalators and moving walkways |  | Not applicable | Not applicable
Note: This table does not include sanitaryware – this may be updated in the future